**Recessed thermostatic sequential shower mixer with angled outlet**

SECURITHERM mixer with no non-return valves, kit 2/2

Without shower head

Reference: **H9633L**

Specification description

Recessed SECURITHERM thermostatic shower with elbow outlet, kit 2/2 :

Thermostatic sequential mixer: opens and closes with cold water.

Mixer with no non-return valves on the inlets (reduces bacterial proliferation).

No risk of cross flow between hot and cold water.

Sequential mixer with anti-scalding failsafe: shuts off automatically if cold water supply fails.

Prevents cold showers: cold water supply shuts off if hot water supply fails.

Sequential mixer with Securitouch thermal insulation prevents burns.

Scale-resistant thermostatic sequential cartridge adjusts the flow rate and temperature.

Temperature control from cold water up to 39°C with maximum temperature limiter set at 39°C.

Thermal shocks are possible.

Flow rate regulated at 9 lpm (mixer only), 6 lpm at 3 bar with shower head.

Hygiene lever L. 100mm.

Filters integrated on the inlets M3/4".

Order a shower head or wall outlet.

Bright polished stainless steel wall plate 166 x 166mm.

Mixer ideal for healthcare facilities, retirement and care homes, hospitals and clinics.

Sequential mixer suitable for people with reduced mobility.

Shower mixer with 30-year warranty.

Order the waterproof recessing housing ref. H96CBOX.